## Modèles acceptables
LISTE DES MODÈLES ACCEPTÉS PAR LE COORDONNATEUR DE LA PLANIFICATION POUR LA MODÉLISATION DE L'INTERCONNEXION DU QUÉBEC
BASÉE SUR LA LISTE DES MODÈLES ACCEPTÉS PAR LA NERC
L'utilisation de ce modèle n'est pas recommandé. D'autres modèles conviennent davantage.
L'utilisation de ce modèle est considéré inacceptable. Sauf sur entente avec le Coordonnateur de la planification, la soumission de nouveaux paramètres pour ce modèle est interdit. Limitations ou divergences connues.
Type de modèle | Description du modèle | Modèle inacceptable | Siemens PTI PSS/e (v. 34) | Commentaires | Référence
Modèle de machine | Round Rotor Generator Model (IEEE Std 1110 §5.3.2 Model 2.2) |  | GENROU | Traitement de la saturation. Utiliser GENTPJ. Voir le "Modeling Notification". | Modeling Notification - Use of GENTPJ
| Salient Pole Generator Model (IEEE Std 1110 §5.3.1 Model 2.1) | ü | GENSAL | Traitement de la saturation. Utiliser GENTPJ. Voir le "Modeling Notification". | Modeling Notification - Use of GENTPJ
| Round Rotor Generator Model (IEEE Std 1110 §5.3.2 Model 2.2) |  | GENROE | Traitement de la saturation. Utiliser GENTPJ. Voir le "Modeling Notification". | Modeling Notification - Use of GENTPJ
| Salient Pole Generator Model (IEEE Std 1110 §5.3.1 Model 2.1) |  | GENSAE | Traitement de la saturation. Utiliser GENTPJ. Voir le "Modeling Notification". | Modeling Notification - Use of GENTPJ
| Round Rotor Generator with DC Offset Torque Component |  | GENDCO
| Generator Type J |  | GENTPJU1
| Classical Generator Model (IEEE Std 1110 §5.4.2) | ü | GENCLS | Ne permet pas la représentation du système d'excitation et du régulateur de vitesse. | SME input.
| Transient Level Generator Model | ü | GENTRA | Modèle simplifié sans les effets sous-transitoire. Sujet à des problèmes numériques. | PSS/E PAG V2, Section 14.4.5.4
| Salient Pole Frequency Changer Model |  | FRECHG
| "Two-cage" or "One-Cage" Induction Generator |  | CIMTR1, CIMTR3
Signal Playback Models | Play-In of Voltage and/or Frequency Signal |  | PLBVFU1
| Frequency Playback Model |  | TSTGOV1
Modèle de ressource de production renouvelable | Generic Type 1 WTG Generator Model (Fixed-speed induction generator) |  | WT1G1
| Generic Type 2 WTG Generator Model (Variable slip induction generator with variable rotor resistance) |  | WT2G1
| Generic Type 3 WTG Generator/Converter Model - PSSE (Doubly-fed induction generator) | ü | WT3G1 | Les modèles de ressources renouvelables de seconde génétarion remplacent ces modèle. Problèmes numériques. | WECC Wind Modeling Guideline
| Generic Type 3 WTG Generator/Converter Model - PSLF (Doubly-fed induction generator) | ü | WT3G2 | Les modèles de ressources renouvelables de seconde génétarion remplacent ces modèle. Problèmes numériques. | WECC Wind Modeling Guideline
| Generic Type 4 WTG Generator/Converter Model - PSSE (Variable speed generator with full converter) | ü | WT4G1 | Les modèles de ressources renouvelables de seconde génétarion remplacent ces modèle. Problèmes numériques. | WECC Wind Modeling Guideline
| Generic Type 4 WTG Generator/Converter Model - PSLF (Variable speed generator with full converter) | ü | WT4G2 | Les modèles de ressources renouvelables de seconde génétarion remplacent ces modèle. Problèmes numériques. | WECC Wind Modeling Guideline
| Generic Type 2 WTG Rotor Resistance Control Model |  | WT2E1
| Generic Type 3 WTG Electrical Control Model | ü | WT3E1 | Les modèles de ressources renouvelables de seconde génétarion remplacent ces modèle. Problèmes numériques. | WECC Wind Modeling Guideline
| Generic Type 4 WTG Electrical Control Model - PSSE | ü | WT4E1 | Les modèles de ressources renouvelables de seconde génétarion remplacent ces modèle. Problèmes numériques. | WECC Wind Modeling Guideline
| Generic Type 4 WTG Electrical Control Model - PSLF | ü | WT4E2 | Les modèles de ressources renouvelables de seconde génétarion remplacent ces modèle. Problèmes numériques.
| Generic Type 1 Two Mass Turbine Model |  | WT12T1
| Generic Type 2 Two Mass Turbine Model |  | WT12T1
| Generic Type 3 WTG Turbine Model | ü | WT3T1 | Les modèles de ressources renouvelables de seconde génétarion remplacent ces modèle. Problèmes numériques. | WECC Wind Modeling Guideline
| Generic Type 3 and 4 WTG Drive Train Model |  | WTDTAU1
| Generic Type 3 WTG Pitch Control Model | ü | WT3P1 | Les modèles de ressources renouvelables de seconde génétarion remplacent ces modèle. Problèmes numériques. | WECC Wind Modeling Guideline
| Generic Type 3 and 4 WTG Pitch Control Model |  | WTPTAU1
| Generic Type 1 and 2 WTG Pitch Control Model | ü | WT12A1 | Ne représente pas de façon précise les contrôles des WTG type 1. | SME input.
| Generic Type 3 and 4 WTG Aerodynamics Model |  | WTARAU1
| Generic Type 3 and 4 WTG Torque Control Model |  | WTTQAU1
| Linearized Model of PV Panel Output Curve |  | PANELU1
| Linearized Model of PV Panel Solar Irradiance Profile |  | IRRADU1
| Generic Phase 2 Renewable Energy Generator/Converter Model |  | REGCAU1
| Generic Phase 2 Renewable Energy Electrical Controls Model |  | REECAU1
| Generic Phase 2 Renewable Energy Plant Controller |  | REPCAU1
| Generic Phase 2 PV Electrical Controls Model |  | REECBU1 | Utiliser REECA pour représenter l'équipement. Ce modèle manque la logique VDL, notamment l'arrêt temporaire. | Modeling Notification
| Generic Phase 2 Renewable Energy Auxiliary Control Model - Type 3 WTGs |  | REAX3BU1
| Generic Phase 2 Renewable Energy Auxiliary Control Model - Type 4 WTGs and Solar PV |  | REAX4BU1
| Generic Phase 2 Renewable Energy Auxiliary Control Model - SVC |  | SVCAXBU1
| Generic Phase 2 Renewable Energy Auxiliary Control Model - FACTS Device |  | FCTAXBU1
| Generic Phase 2 Renewable Energy Auxiliary Control Model - Synchronous Condenser |  | SYNAXBU1
| Solar Photovoltaic Generator/Converter Model |  | PVGU1
| Solar Photovoltaic Electrical Control Model |  | PVEU1
| Distributed Energy Resource Generator/Converter Model |  | DERAU1 |  | https://www.wecc.org/Reliability/DER_A_Final_061919.pdf
Modèle de système d'excitation | IEEE Std 421.5 Type AC1A |  | ESAC1A
| Modified IEEE Std 421.5 Type AC1A |  | ESURRY
| IEEE Std 421.5 Type AC2A |  | ESAC2A
| IEEE Std 421.5 Type AC3A |  | ESAC3A
| IEEE Std 421.5 Type AC4A |  | ESAC4A
| IEEE Std 421.5 Type AC5A |  | ESAC5A
| IEEE Std 421.5 Type AC6A |  | ESAC6A | Problème avec les limites VAMAX et VAMIN. Ne correspond pas au standard IEEE. | https://siemens.force.com/SEMC2/s/article/PSS-E-User-Support
| IEEE Std 421.5 Type AC6A |  | AC6A
| IEEE Std 421.5 Type AC7B* |  | AC7B
| IEEE Std 421.5 Type AC8B |  | AC8B
| Modified IEEE Std 421.5 Type AC8B |  | ESAC8B
| IEEE Std 421.5 Type DC1A |  | ESDC1A
| IEEE Std 421.5 Type DC2A |  | ESDC2A
| IEEE Std 421.5 Type DC3A |  | DC3A
| IEEE Std 421.5 Type DC4B |  | DC4B
| IEEE Std 421.5 Type ST1A |  | ESST1A
| IEEE Std 421.5 Type ST2A |  | ESST2A
| IEEE Std 421.5 Type ST3A |  | ESST3A
| IEEE Std 421.5 Type ST4B |  | ESST4B
| IEEE Std 421.5 Type ST5B** |  | ST5B
| IEEE Proposed Type ST5B Excitation System |  | URST5T
| IEEE Std 421.5 Type ST6B |  | ST6B
| IEEE Std 421.5 Type ST7B |  | ST7B
| 1968 IEEE Type 1+B127 |  | IEEET1
| Modified 1968 IEEE Type 1 |  | IEET1A
| Modified 1968 IEEE Type 1 |  | IEET1B
| 1968 IEEE Type 2 |  | IEEET2
| 1968 IEEE Type 3 |  | IEEET3
| 1968 IEEE Type 4 |  | IEEET4
| Modified 1968 IEEE Type 4 |  | IEEET5
| Modified 1968 IEEE Type 4 |  | IEET5A
| 1981 IEEE Type AC1 |  | EXAC1
| Modified 1981 IEEE Type AC1 (modified rate feedback source and with added speed multiplier) |  | EXAC1A
| 1981 IEEE Type AC2 |  | EXAC2
| 1981 IEEE Type AC3 |  | EXAC3
| Modified 1981 IEEE Type AC3 |  | ESAC3A
| 1981 IEEE Type AC4 |  | EXAC4
| 1981 IEEE Type DC1 |  | IEEEX1
| Modified 1981 IEEE Type DC1 |  | IEEEX2
| Modified 1981 IEEE Type DC1 |  | IEEX2A
| 1981 IEEE Type DC2 |  | EXDC2
| Modified 1981 IEEE Type DC2 |  | IEEEX2
| 1981 IEEE Type DC3 |  | IEEEX4
| 1981 IEEE Type ST1 |  | EXST1
| 1981 IEEE Type ST2 |  | EXST2
| Modified 1981 IEEE Type ST2 |  | EXST2A
| Modified 1981 IEEE Type ST2 |  | IEEEX3
| 1981 IEEE Type ST3 |  | EXST3
| Modified 1981 IEEE Type ST3 |  | ESST3A
| General Purpose Rotating Excitation System Model |  | REXSYS
| General Purpose Rotating Excitation System Model |  | REXSY1
| Proportional/Integral Excitation System Model |  | EXPIC1
| Bus or Solid Fed SCR Bridge Excitation System Model |  | SCRX
| Bus or Solid Fed SCR Bridge Excitation System Model Type NEBB (NVE) |  | EXNEBB
| Bus or Solid Fed SCR Bridge Excitation System Model Type NI (NVE) |  | EXNI
| IVO Excitation System Model |  | IVOEX
| ELIN Excitation System |  | CELIN
| Basler Static Voltage Regulator Feeding DC or AC Rotating Exciter |  | EXBAS
| Brown-Boveri Transformer-Fed Static Excitation System Model |  | BBSEX1
| Static PI Transformer Fed Excitation System |  | EXELI
| AEP Rockport excitation system |  | EMAC1T
| Czech Proportional/Integral Excitation System Model |  | BUDCZT
| High Dam Excitation System Model |  | URHIDT
Stabilisateur | Transient Excitation Boosting Stabilizer Model |  | BEPSST
| Dual-Input Signal Power System Stabilizer Model |  | IEE2ST
| 1981 IEEE Power System Stabilizer |  | IEEEST
| IVO Stabilizer Model |  | IVOST
| Ontario Hydro Delta-Omega Power System Stabilizer |  | OSTB2T
| Ontario Hydro Delta-Omega Power System Stabilizer |  | OSTB5T
| IEEE Std 421.5-2005 Single-Input Stabilizer Model |  | PSS1A
| 1992 IEEE Type Dual-Input Signal Stabilizer Model |  | PSS2A
| IEEE Std 421.5-2005 PSS2B Dual-Input Stabilizer Model |  | PSS2B
| IEEE Std 421.5-2005 PSS3B Dual-Input Stabilizer Model |  | PSS3B
| IEEE Std 421.5-2005 PSS4B Dual-Input Stabilizer Model |  | PSS4B
| PTI Microprocess-Based Stabilizer Model |  | PTIST1
| PTI Microprocess-Based Stabilizer Model |  | PTIST3
| Speed Sensitive Stabilizer Model |  | STAB1
| ASEA Power Sensitive Stabilizer Model |  | STAB2A
| Power Sensitive Stabilizer Model |  | STAB3
| Power Sensitive Stabilizer Model |  | STAB4
| Dual-Input Signal Power System Stabilizer Model |  | ST2CUT
| WECC Supplementary Signal for Static Var System |  | STBSVC
| Synchronous Condenser Auxiliary Control Model |  | SYNAXBU1
Modèles de compensation en courant | Cross-Current Compensation Model with Reactive Current Feedback |  | CCOMP4U1
| Voltage Regulator Compensating Model |  | COMP
| Cross and Joint Current Compensation Model |  | COMPCC
| IEEE Std 421.5 Current Compensator |  | IEEEVC
| Remote Bus Voltage Signal Model |  | REMCMP
Modèles de turbine / régulateur de vitesse | Combined Cycle Plant Steam Turbine Model |  | UCBGT
| General Purpose (Gas Turbine & Single Shaft CC) Turbine-Governor Model |  | GGOV1^
| Brown-Boveri Turbine-Governor Model |  | BBGOV1
| Cross Compound Turbine-Governor Model |  | CRCMGV
| Woodward Diesel Governor Model |  | DEGOV
| Woodward Diesel Governor Model |  | DEGOV1^
| Gas Turbine-Governor Model | ü | GAST^ | Représentation simple du système de contrôle d'une turbine/directrice. Capacité et flexibilité insuffisante pour la plupart des systèmes de contrôle numériques modernes. | Modeling Notification - Gas Turbine Governor Modeling
| Gas Turbine-Governor Model | ü | GAST2A^ | Représentation simple du système de contrôle d'une turbine/directrice. Capacité et flexibilité insuffisante pour la plupart des systèmes de contrôle numériques modernes. | Modeling Notification - Gas Turbine Governor Modeling
| Gas turbine-governor | ü | GASTWD^ | Représentation simple du système de contrôle d'une turbine/directrice. Capacité et flexibilité insuffisante pour la plupart des systèmes de contrôle numériques modernes. | Modeling Notification - Gas Turbine Governor Modeling
| Hydro Turbine-Governor Model |  | HYGOV^
| Hydro Turbine-Governor Model |  | HYGOV2^ | Remplacé par le modèle hygov4 ou tout autre modèle hydraulique à jour.
| Hydro Turbine-Governor Lumped Parameter Model |  | HYGOVM
| Fourth Order Lead-Lag Hydro-Turbine Model |  | HYGOVR1
| Hydro Turbine-Governor Traveling Wave Model |  | HYGOVT
| 1981 IEEE Type 1 General Steam Turbine-Governor Model |  | IEEEG1^ | Utiliser le modèle WSIEG1 à la place
| 1981 IEEE Type 2 General Approx. Linear Ideal Hydro Model | ü | IEEEG2 | Ce modèle n'a pas un modèle de turbine efficace et un modèle de directrice sur-simplifié qui ne s'applique qu'à la stabilité de la premièe oscillation. Périmé. Il est typiquement recommandé d'utiliser un modèle hygov à la place (sans toutefois utiliser les mêmes paramètres)
| 1981 IEEE Type 3 General Mechanical-Hydraulic Model |  | IEEEG3^
| Hydro Turbine-Governor (plants with straightforward penstock config + hydraulic govs of 'dashpot' type) |  | IEEEG3
| IVO Turbine-Governor Model |  | IVOGO
| Hydro Turbine-Governor Model |  | PIDGOV^
| Pratt & Whitney Turboden Turbine-Governor Model |  | PWTBDU1
| Torsional-Elastic Shaft Model for 25 Masses |  | SHAF25
| Steam Turbine-Governor Model |  | TGOV1^
| Czech Hydro or Steam Turbine-Governor Model |  | TURCZT
| Tail Water Depression Hydro Governor Model 1 |  | TWDM1T
| Tail Water Depression Hydro Governor Model 2 |  | TWDM2T
| Combined Cycle - Single Shaft Turbine-Governor Model |  | URCSCT
| Woodward Electronic Hydro Governor Model |  | WEHGOV
| Woodward PID Hydro Governor Model |  | WPIDHY^
| WECC Double Derivative Hydro Governor Model |  | WSHYDD
| PID Governor, Double-Derivative Governor, and Turbine (WECC GP governor, WECC G2 turbine-governor) |  | WSHYGP
| Modified IEEE Type 1 General Steam Turbine-Governor Model w/ Speed Deadband |  | WSIEG1
Modèles de contrôleur de charge | Turbine Load Controller Model |  | LCFB1
Modèles de charge | Induction Generator Model with Rotor Flux Transients |  | CIMTR1
| Induction Motor Model with Rotor Flux Transients |  | CIMTR2
| Induction Generator Model with Rotor Flux Transients |  | CIMTR3
| Induction Motor Model with Rotor Flux Transients |  | CIMTR4
| Induction Motor Model |  | CIM5BL
| Induction Motor Model |  | CIM6BL
| Induction Motor Model |  | CIMWBL
| IEEE Load Model |  | IEEL__
| Load Frequency Model |  | LDFR__
| Extended-Term Load Reset Model |  | EXTLBL
| Complex Load Model |  | CLOD__
| Composite Load Model |  | CMLDBLU1
| Performance-Based Model of Single Phase Air Conditioner Motor Model |  | ACMTBLU1
Compensateur statique et FACTS | WECC Generic Continuous Control SVC Model |  | SVSMO1U2
| WECC Generic Discrete Control SVC Model |  | SVSMO2U2
| WECC Generic STATCOM-Based SVC Model |  | SVSMO3U2
| SCR Controlled Static VAR Source Model |  | CSVGN1
| SCR Controlled Static VAR Source Model |  | CSVGN3
| SCR Controlled Static VAR Source Model |  | CSVGN4
| WECC Controlled Static VAR Source Model |  | CSVGN5
| WECC Controlled Static VAR Source Model |  | CSVGN6
| Switched Shunt Model |  | SWSHNT
| American Superconductor DSMES Device |  | CDSMS1
| Static Condenser FACTS Model |  | CSTATT
| Static Condenser (modeled as FACTS in power flow) |  | CSTCNT
| ABB SVC Model |  | ABBSVC1
| SVC for Switched Shunt |  | CHSVCT
| SVC for Switched Shunt |  | CSSCST
| EPRI Superconducting Electromagnetic Energy Storage FACTS Model |  | CSMEST
| EPRI Battery Energy Storage FACTS Model |  | CBEST
Limiteur de sur/sous excitation | Under-/Over-Frequency Generator Bus Disconnection Relay |  | FRQTPAT
| Under-/Over-Frequency Generator Trip Relay |  | FRQDCAT
| Under-/Over-Voltage Generator Bus Disconnection Relay |  | VTGTPAT
| Under-/Over-Voltage Generator Trip Relay |  | VTGDCAT
| Time-Inverse Overcurrent Relay |  | TIOCR1
| Definite Time Underfrequency Load Shedding Relay |  | LDS3BL
| Definite Time Undervoltage Load Shedding Relay |  | LDS3BL
| Definite Time Undervoltage Load Shedding Relay |  | LDS3BL
| Switched Capacitor Bank Model |  | SWCAPT
| Load Tap Changer Model |  | OLTC1T
| Variable Frequency Transformer or Rotary Phase Shift Regulator |  | OLPS1T
† - Le compensateur de courant fait partie du modèle de machine
* PSSE: Area-based: __=AR; Bus-based: __=BL; Zone-based: __=ZN; All: __=AL
^ For Siemens PTI PSS®E implementation, the "DU" version of the model is also acceptable.
Références supplémentaires
[1] "IEEE Guide for Synchronous Generator Modeling Practices and Applications in Power System Stability Analyses," IEEE Std 1110-2002.
[2] Undrill, J., "The gentpj model," November 19, 2007 (updated June 19, 2012). http://www.wecc.biz/
[3] "IEEE Recommended Practice for Excitation System Models for Power System Stability Studies," IEEE Std 421.5-2005.
[4] “Computer Representation of Excitation Systems," IEEE Transactions on Power Apparatus and Systems, Vol. PAS-87, No. 6, pp. 1460-1468, 1968 (Committee Report).
[5] "Excitation System Models for Power System Stability Studies," IEEE Transactions on Power Apparatus and Systems, Vol. PAS-100, No. 2, pp. 494-509, 1981 (Committee Report).
[6] IEEE Task Force on Overall Plant Response, “Dynamic Models for Steam and Hydro Turbines in Power System Studies”, IEEE Trans. on PAS, Vol PAS-92, Nov-Dec 1973, pp. 1904-1915.
[7] Task Force on Turbine-Governor Modeling, "Dynamic Models for Turbine-Governors in Power System Studies," IEEE Technical Report, PES-TR1, Jan. 2013.
[8] WECC M&VWG, "Composite Load Model for Dynamic Simulations" Ver 1.0, June 12, 2012.
[9] WECC M&VWG, "WECC Wind Power Plant Dynamic Modeling Guide," November 2010.
[10] EPRI, "Specification of the Second Generation Generic Models for Wind Turbine Generators," September 20, 2013. and WECC M&VWG, "Generic Solar Photovoltaic System Dynamic Simulation Model Specification," September 2012.
[11] WECC, "Generic Static Var System Models for the Western Electricity Coordinating Council" April 18, 2011.
[12] W. I. Rowen, “Simplified Mathematical Representations of Heavy Duty Gas Turbines”, ASME Paper 83‐GT‐63 and ASME Journal of Engineering for Power, October 1983, pages 865‐869. [GAST2A reference]
[13] Periera, L. et al, "A New Thermal Governing Approach in the WECC," IEEE Transaction on Power System, Vol. 18, No. 2, pp. 819-829, May 2003.
[14] WECC M&VWG, "Cross-current Compensation Model Specification," August 2015.
[15] EPRI, "Simple Model Specification for Battery Energy Storage System," March 6, 2015.
[W1] WECC Approved Dynamic Model Library. http://www.wecc.biz/
[W2] WECC M&VWG, "WECC Wind Power Plant Dynamic Modeling Guide," April 2014.
[W3] WECC M&VWG, "WECC PV Power Plant Dynamic Modeling Guide," April 2014.
[E1] EPRI, "Proposed Changes to the WECC WT3 Generic Model for Type 3 Wind Turbine Generators," September 27, 2013.
[E2] EPRI, "Proposed Changes to the WECC WT4 Generic Model for Type 4 Wind Turbine Generators," January 23, 2013.
Note on D13: Auteur: GENTPJU1 (v.33), GENTPJ (v.34)
Note on D33: Auteur: WTDTAU1 (v. 33) / WTDTA1 (v. 34)
Note on D35: Auteur: WTPTAU1 (v. 33) / WTPTA1 (v. 34)
Note on D37: Auteur: WTARAU1 (v.33) / WTARA1 (v.34)
Note on D38: Auteur: WTTQAU1 (v. 33) / WTTQA1 (v. 34)
Note on D41: Auteur: REGCAU1 (v. 33) / REGCA1 (v. 34)
Note on D42: Auteur: REECAU1 (v. 33) / REECA1 (v. 34)
Note on D43: Auteur: REPCTAU1 (v. 33) / REPCTA1 (v. 34) for Type 3;
Note on D44: Auteur: REECBU1 (v. 33) / REECB1 (v. 34)
Note on D46: Auteur: REAX4BU1 for Type 4; REAX3BU1 for Type 3
Note on D60: Auteur: in version 34. Until then, use the USAC6AU model.
Note on D141: Auteur: Model from PTI
Note on D187: Auteur: SVSMO1U2 (v. 33) / SVSMO1T2 (v. 34)
Note on D188: Auteur: SVSMO2U2 (v. 33) / SVSMO2T2 (v. 34)
Note on D189: Auteur: SVSMO3U2 (v. 33) / SVSMO3T2 (v. 34)

## Suivi des versions
LISTE DES MODÈLES ACCEPTÉS PAR LE COORDONNATEUR DE LA PLANIFICATION POUR LA MODÉLISATION DE L'INTERCONNEXION DU QUÉBEC
Dernière révision : Novembre 2020
| Version | Date | Description
| 1 | 2020-11-05 | Première version
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25